## Legend
Wind + BESS 115 kV Interconnection — Calculation Workbook
PRELIMINARY ENGINEERING — NOT FOR CONSTRUCTION ¦ Rev P0 ¦ 2026-10-13
Purpose | Traceable formulas supporting the preliminary engineering report (Appendix A).
Blue text | Hard-coded inputs (edit only on sheet "Inputs").
Black text | Formulas — do not overwrite.
Yellow fill | Engineering assumption / parametric value requiring OEM, site or utility confirmation.
Green fill | Frozen project data supplied by the client.
Flags | F = frozen project data ¦ A = engineering assumption ¦ P = parametric/illustrative ¦ O = OEM to confirm ¦ U = utility to confirm
Independent check | Sheet "Check" compares each key workbook result with the separate Python engine (calc.py). ¦Δ¦ must be < 0.5 %.
Status | No site cable lengths, soil thermal data, utility fault levels, OEM impedances or PCS data were available. Values depending on these are screening values only.

## Inputs
Inputs
PRELIMINARY ENGINEERING — NOT FOR CONSTRUCTION ¦ Rev P0 ¦ 2026-10-13
Parameter | Symbol | Value | Unit | Flag | Basis / source
Number of WTGs | N_WTG | 27 | - | F | Client frozen data
WTG rated active power | P_WTG | 3.8 | MW | F | Client frozen data (GE Vernova DFIG; model TBC by OEM)
WTG reactive capability at rated P (PF) | PF_WTG | 0.95 | - | A/O | Screening for kVA/current sizing; confirm GE Vernova P-Q capability chart
WTG LV voltage | V_LV | 0.69 | kV | F | Client frozen data
Collector voltage | V_MV | 34.5 | kV | F | Client frozen data
POI voltage | V_HV | 115 | kV | F | Client frozen data
Minimum steady-state voltage for current sizing | V_MIN | 0.95 | pu | A | Screening; confirm with load-flow and SoCo voltage schedule
WTGs on WF-01 | N_F1 | 7 | - | F | Client
WTGs on WF-02 | N_F2 | 7 | - | F | Client
WTGs on WF-03 | N_F3 | 7 | - | F | Client
WTGs on WF-04 | N_F4 | 6 | - | F | Client
POI export limit | P_EXP | 100 | MW | F | Client
POI import limit | P_IMP | 100 | MW | F | Client
POI reactive requirement (PF) | PF_POI | 0.95 | - | A/U | FERC Order 827 pro-forma LGIA ±0.95 at high side of generator substation unless SoCo specifies otherwise
BESS rated power | P_BESS | 100 | MW | F | Client
BESS energy | E_BESS | 200 | MWh | F | Client
BESS PF at MV for feeder sizing | PF_BESS | 0.95 | - | A/O | PCS configuration not provided — replace with actual PCS MVA
Number of BESS feeders | N_BF | 4 | - | F | Client (existing design, unchanged)
GSU candidate top rating | S_GSU | 125 | MVA | P | Candidate only — not an approved selection
GSU impedance (on S_GSU base) | Z_GSU | 0.1 | pu | P | Parametric; range 0.08–0.12 evaluated; transformer vendor/utility study
GSU load loss at S_GSU | PCU_GSU | 0.004 | pu | A | Screening; replace with vendor guarantee
Grid short-circuit level at 115 kV | S_SC | 8000 | MVA | P | NOT PROVIDED by utility — parametric (∞ also evaluated)
DFIG fault multiplier (bounding) | K_DFIG | 5 | pu | A/O | Bounding screening value; GE Vernova to provide fault-current data
BESS PCS fault multiplier | K_IBR | 1.2 | pu | A/O | Typical IBR current limit; PCS OEM to confirm
Al resistivity at 20 °C | RHO_AL | 2.8264e-08 | Ω·m | A | IEC 60028 / ASTM B609 1350 Al
Stranding/compaction factor | K_STR | 1.02 | - | A | Screening
Al temperature coefficient | ALPHA_AL | 0.00403 | 1/°C | A | IEC 60287-1-1 Table 1
Insulation thickness (35 kV, 133 %) | T_INS | 10.67 | mm | A | ICEA S-94-649 420 mil; 100 % level (345 mil) is an alternative open item
Conductor screen thickness | T_CS | 0.6 | mm | A | Typical
Insulation screen thickness | T_IS | 1 | mm | A | Typical
Concentric neutral wire diameter (#12 AWG) | D_W | 2.053 | mm | A | Typical
Number of neutral wires | N_W | 11 | - | A | ≈36 mm² Cu; fault rating to be confirmed
Jacket thickness | T_J | 2.03 | mm | A | 80 mil LLDPE
Insulation relative permittivity | EPS | 2.5 | - | A | IEC 60287-1-1 (XLPE/TR-XLPE)
Dielectric loss factor tanδ | TAND | 0.004 | - | A | IEC 60287-1-1
Insulation thermal resistivity | RHO_I | 3.5 | K·m/W | A | IEC 60287-2-1
Jacket thermal resistivity | RHO_J | 3.5 | K·m/W | A | IEC 60287-2-1
Native soil thermal resistivity (design) | RHO_S | 1.2 | K·m/W | A | NO SITE DATA — thermal survey (IEEE 442) required; sensitivity 0.9–2.0 shown
Ambient earth temperature at burial depth | T_AMB | 25 | °C | A | NO SITE DATA — confirm
Burial depth to trefoil centre | DEPTH | 1 | m | A | ≥ NESC minimum cover; confirm
Conductor max operating temperature | T_MAX | 90 | °C | A | ICEA S-94-649 XLPE/EPR
Screen operating temperature | T_SCR | 80 | °C | A | Screening
Frequency | FREQ | 60 | Hz | F | US grid
Grouped-corridor circuit spacing (4 trefoils, flat) | GSP | 2 | m | A | Substation approach corridor; confirm with layout
Illustrative inter-WTG section length | L_INT | 0.616 | km | P | ILLUSTRATIVE = 4 × 154 m rotor; NOT SITE DATA
Illustrative home-run length | L_HR | 5 | km | P | ILLUSTRATIVE; NOT SITE DATA
Internal loss fraction — wind path to POI | LOSS_W | 0.03 | pu | A | Screening for scenarios
Internal loss fraction — BESS path to POI | LOSS_B | 0.015 | pu | A | Screening
Auxiliary/station load | AUX | 1 | MW | A | Placeholder pending aux load list (incl. BESS HVAC)

## WTG
WTG electrical quantities and step-up transformer kVA
PRELIMINARY ENGINEERING — NOT FOR CONSTRUCTION ¦ Rev P0 ¦ 2026-10-13
Quantity | Equation | Value | Unit
Apparent power S_WTG | S = P / PF | 4 | MVA
Reactive power Q_WTG | Q = √(S²−P²) | 1.249 | Mvar
LV current, unity PF | I = P/(√3·V) | 3179.6102 | A
LV current at S_WTG | I = S/(√3·V) | 3346.9581 | A
LV current at S_WTG, V_MIN | I = S/(√3·V·Vpu) | 3523.1138 | A
MV current, unity PF | I = P/(√3·34.5 kV) | 63.5922 | A
MV current at S_WTG |  | 66.9392 | A
MV current at S_WTG, V_MIN |  | 70.4623 | A
Minimum WTG transformer rating | S_T ≥ S_WTG (+aux, harmonics per OEM) | 4 | MVA
Gross wind P | ΣP | 102.6 | MW
Gross wind S | ΣS | 108 | MVA
Gross wind MV current |  | 1807.3574 | A

## Cable_Ampacity
Cable parameters & IEC 60287 steady-state ampacity — 35 kV Al, 3×1C trefoil touching, direct buried, solidly bonded
PRELIMINARY ENGINEERING — NOT FOR CONSTRUCTION ¦ Rev P0 ¦ 2026-10-13
Size | A (mm²) | dc (mm) | R20 (Ω/m) | R'90 (Ω/m) | xs⁴ | ys | xp⁴ | dc/s | yp | Rac90 (Ω/m) | Di (mm) | dS (mm) | Da (mm) | De (mm) | C (F/m) | Wd (W/m) | As (mm²) | Rs (Ω/m) | Xs (Ω/m) | λ1 | T1 | T3 | u | T4 | Ampacity (A) | X (Ω/m) | Qc (kvar/km) | Rac (Ω/km) | X (Ω/km) | T4 grouped | Ampacity grouped (A)
1/0 AWG | 53.49 | 8.53 | 0.00053897 | 0.00069101 | 0.047623 | 0.00024799 | 0.030479 | 0.20686 | 2.9756e-05 | 0.0006912 | 31.07 | 35.123 | 37.176 | 41.236 | 1.1963e-10 | 0.07157 | 36.4133 | 0.00058513 | 6.436e-05 | 0.010119 | 0.75481 | 0.057736 | 48.5013 | 2.2602 | 174.019 | 0.00018992 | 53.6777 | 0.6912 | 0.18992 | 2.7212 | 162.2024
4/0 AWG | 107.2 | 12.07 | 0.00026893 | 0.00034479 | 0.19128 | 0.00099544 | 0.12242 | 0.26956 | 0.00020295 | 0.00034521 | 34.61 | 38.663 | 40.716 | 44.776 | 1.4488e-10 | 0.086681 | 36.4133 | 0.00058513 | 6.333e-05 | 0.019626 | 0.61809 | 0.052948 | 44.6668 | 2.213 | 253.1322 | 0.00016995 | 65.0104 | 0.34521 | 0.16995 | 2.674 | 234.9008
350 kcmil | 177.3 | 15.65 | 0.0001626 | 0.00020847 | 0.52322 | 0.0027192 | 0.33486 | 0.32364 | 0.00079813 | 0.0002092 | 38.19 | 42.243 | 44.296 | 48.356 | 1.6974e-10 | 0.10156 | 36.4133 | 0.00058513 | 6.2452e-05 | 0.031503 | 0.52537 | 0.04885 | 41.3599 | 2.1689 | 331.698 | 0.00015617 | 76.1667 | 0.2092 | 0.15617 | 2.63 | 306.6658
500 kcmil | 253.4 | 18.69 | 0.00011377 | 0.00014586 | 1.0688 | 0.0055418 | 0.68401 | 0.36365 | 0.0020458 | 0.00014697 | 41.23 | 45.283 | 47.336 | 51.396 | 1.9053e-10 | 0.11399 | 36.4133 | 0.00058513 | 6.181e-05 | 0.043935 | 0.46711 | 0.045839 | 38.9135 | 2.134 | 400.7111 | 0.00014738 | 85.4948 | 0.14697 | 0.14738 | 2.595 | 369.4406
750 kcmil | 380 | 23.06 | 7.5867e-05 | 9.7268e-05 | 2.4035 | 0.012394 | 1.5382 | 0.41351 | 0.0058512 | 9.9043e-05 | 45.6 | 49.653 | 51.706 | 55.766 | 2.2008e-10 | 0.13167 | 36.4133 | 0.00058513 | 6.1016e-05 | 0.06355 | 0.40371 | 0.042107 | 35.8641 | 2.0872 | 494.7604 | 0.00013769 | 98.7537 | 0.099043 | 0.13769 | 2.5483 | 454.524
1000 kcmil | 506.7 | 26.92 | 5.6896e-05 | 7.2947e-05 | 4.2734 | 0.021868 | 2.735 | 0.45148 | 0.012107 | 7.5425e-05 | 49.46 | 53.513 | 55.566 | 59.626 | 2.4596e-10 | 0.14715 | 36.4133 | 0.00058513 | 6.0418e-05 | 0.081838 | 0.36093 | 0.039283 | 33.5424 | 2.0489 | 572.0482 | 0.00013107 | 110.3651 | 0.075425 | 0.13107 | 2.5099 | 524.0358
1250 kcmil | 633.4 | 30.23 | 4.5515e-05 | 5.8355e-05 | 6.6777 | 0.033838 | 4.2737 | 0.48033 | 0.020762 | 6.1541e-05 | 52.77 | 56.823 | 58.876 | 62.936 | 2.6803e-10 | 0.16036 | 36.4133 | 0.00058513 | 5.9966e-05 | 0.098823 | 0.33105 | 0.037146 | 31.7783 | 2.0179 | 636.9388 | 0.0001264 | 120.2697 | 0.061541 | 0.1264 | 2.479 | 582.1611
Notes
Method: IEC 60287-1-1 (losses) and IEC 60287-2-1 (thermal resistances, T4 for equally loaded trefoil touching: T4 = 1.5/π·ρ·[ln(2u) − 0.630]).
100 % load factor assumed (conservative). Wind cyclic rating per IEC 60853 / Neher-McGrath with site LF may justify higher ratings — to be done in CYMCAP/ETAP.
λ1 = circulating-current loss factor for solidly bonded concentric neutrals; eddy losses neglected for wire screens.
Results are SCREENING ONLY: soil thermal resistivity, ambient, depth and duct-bank/crossing hot-spots are not yet known.

## Feeder_Sections
Collector feeder cumulative section currents, minimum conductor size, illustrative voltage drop & losses
PRELIMINARY ENGINEERING — NOT FOR CONSTRUCTION ¦ Rev P0 ¦ 2026-10-13
Feeder | Section # | From node | WTGs carried k | P (MW) | S (MVA) | I @1.0 pu (A) | I @V_MIN (A) | Min. size (ampacity ≥ I@V_MIN; home-run: grouped) | Ampacity (A) | Loading % | Illustr. L (km) | Rac (Ω/km) | X (Ω/km) | ΔV (%) | Loss (kW)
WF-01 | 1 | WF-01-T07 → WF-01-T06 | 1 | 3.8 | 4 | 66.9392 | 70.4623 | 1/0 AWG | 174.019 | 40.49% | 0.616 | 0.6912 | 0.18992 | 0.1482% | 5.7236
WF-01 | 2 | WF-01-T06 → WF-01-T05 | 2 | 7.6 | 8 | 133.8783 | 140.9246 | 1/0 AWG | 174.019 | 80.98% | 0.616 | 0.6912 | 0.18992 | 0.2964% | 22.8942
WF-01 | 3 | WF-01-T05 → WF-01-T04 | 3 | 11.4 | 12 | 200.8175 | 211.3868 | 4/0 AWG | 253.1322 | 83.51% | 0.616 | 0.34521 | 0.16995 | 0.2366% | 25.7268
WF-01 | 4 | WF-01-T04 → WF-01-T03 | 4 | 15.2 | 16 | 267.7566 | 281.8491 | 350 kcmil | 331.698 | 84.97% | 0.616 | 0.2092 | 0.15617 | 0.205% | 27.7175
WF-01 | 5 | WF-01-T03 → WF-01-T02 | 5 | 19 | 20 | 334.6958 | 352.3114 | 500 kcmil | 400.7111 | 87.92% | 0.616 | 0.14697 | 0.14738 | 0.1922% | 30.4253
WF-01 | 6 | WF-01-T02 → WF-01-T01 | 6 | 22.8 | 24 | 401.635 | 422.7737 | 750 kcmil | 494.7604 | 85.45% | 0.616 | 0.099043 | 0.13769 | 0.1703% | 29.525
WF-01 | 7 | WF-01-T01 → SUBSTATION 34.5 kV BUS | 7 | 26.6 | 28 | 468.5741 | 493.2359 | 1000 kcmil | 524.0358 | 94.12% | 5 | 0.075425 | 0.13107 | 1.324% | 248.4064
WF-01 TOTAL |  |  |  | 26.6 |  | 468.5741 | 493.2359 | [6 empty] | 2.573% | 390.4187 | 1.468%
WF-02 | 1 | WF-02-T07 → WF-02-T06 | 1 | 3.8 | 4 | 66.9392 | 70.4623 | 1/0 AWG | 174.019 | 40.49% | 0.616 | 0.6912 | 0.18992 | 0.1482% | 5.7236
WF-02 | 2 | WF-02-T06 → WF-02-T05 | 2 | 7.6 | 8 | 133.8783 | 140.9246 | 1/0 AWG | 174.019 | 80.98% | 0.616 | 0.6912 | 0.18992 | 0.2964% | 22.8942
WF-02 | 3 | WF-02-T05 → WF-02-T04 | 3 | 11.4 | 12 | 200.8175 | 211.3868 | 4/0 AWG | 253.1322 | 83.51% | 0.616 | 0.34521 | 0.16995 | 0.2366% | 25.7268
WF-02 | 4 | WF-02-T04 → WF-02-T03 | 4 | 15.2 | 16 | 267.7566 | 281.8491 | 350 kcmil | 331.698 | 84.97% | 0.616 | 0.2092 | 0.15617 | 0.205% | 27.7175
WF-02 | 5 | WF-02-T03 → WF-02-T02 | 5 | 19 | 20 | 334.6958 | 352.3114 | 500 kcmil | 400.7111 | 87.92% | 0.616 | 0.14697 | 0.14738 | 0.1922% | 30.4253
WF-02 | 6 | WF-02-T02 → WF-02-T01 | 6 | 22.8 | 24 | 401.635 | 422.7737 | 750 kcmil | 494.7604 | 85.45% | 0.616 | 0.099043 | 0.13769 | 0.1703% | 29.525
WF-02 | 7 | WF-02-T01 → SUBSTATION 34.5 kV BUS | 7 | 26.6 | 28 | 468.5741 | 493.2359 | 1000 kcmil | 524.0358 | 94.12% | 5 | 0.075425 | 0.13107 | 1.324% | 248.4064
WF-02 TOTAL |  |  |  | 26.6 |  | 468.5741 | 493.2359 | [6 empty] | 2.573% | 390.4187 | 1.468%
WF-03 | 1 | WF-03-T07 → WF-03-T06 | 1 | 3.8 | 4 | 66.9392 | 70.4623 | 1/0 AWG | 174.019 | 40.49% | 0.616 | 0.6912 | 0.18992 | 0.1482% | 5.7236
WF-03 | 2 | WF-03-T06 → WF-03-T05 | 2 | 7.6 | 8 | 133.8783 | 140.9246 | 1/0 AWG | 174.019 | 80.98% | 0.616 | 0.6912 | 0.18992 | 0.2964% | 22.8942
WF-03 | 3 | WF-03-T05 → WF-03-T04 | 3 | 11.4 | 12 | 200.8175 | 211.3868 | 4/0 AWG | 253.1322 | 83.51% | 0.616 | 0.34521 | 0.16995 | 0.2366% | 25.7268
WF-03 | 4 | WF-03-T04 → WF-03-T03 | 4 | 15.2 | 16 | 267.7566 | 281.8491 | 350 kcmil | 331.698 | 84.97% | 0.616 | 0.2092 | 0.15617 | 0.205% | 27.7175
WF-03 | 5 | WF-03-T03 → WF-03-T02 | 5 | 19 | 20 | 334.6958 | 352.3114 | 500 kcmil | 400.7111 | 87.92% | 0.616 | 0.14697 | 0.14738 | 0.1922% | 30.4253
WF-03 | 6 | WF-03-T02 → WF-03-T01 | 6 | 22.8 | 24 | 401.635 | 422.7737 | 750 kcmil | 494.7604 | 85.45% | 0.616 | 0.099043 | 0.13769 | 0.1703% | 29.525
WF-03 | 7 | WF-03-T01 → SUBSTATION 34.5 kV BUS | 7 | 26.6 | 28 | 468.5741 | 493.2359 | 1000 kcmil | 524.0358 | 94.12% | 5 | 0.075425 | 0.13107 | 1.324% | 248.4064
WF-03 TOTAL |  |  |  | 26.6 |  | 468.5741 | 493.2359 | [6 empty] | 2.573% | 390.4187 | 1.468%
WF-04 | 1 | WF-04-T06 → WF-04-T05 | 1 | 3.8 | 4 | 66.9392 | 70.4623 | 1/0 AWG | 174.019 | 40.49% | 0.616 | 0.6912 | 0.18992 | 0.1482% | 5.7236
WF-04 | 2 | WF-04-T05 → WF-04-T04 | 2 | 7.6 | 8 | 133.8783 | 140.9246 | 1/0 AWG | 174.019 | 80.98% | 0.616 | 0.6912 | 0.18992 | 0.2964% | 22.8942
WF-04 | 3 | WF-04-T04 → WF-04-T03 | 3 | 11.4 | 12 | 200.8175 | 211.3868 | 4/0 AWG | 253.1322 | 83.51% | 0.616 | 0.34521 | 0.16995 | 0.2366% | 25.7268
WF-04 | 4 | WF-04-T03 → WF-04-T02 | 4 | 15.2 | 16 | 267.7566 | 281.8491 | 350 kcmil | 331.698 | 84.97% | 0.616 | 0.2092 | 0.15617 | 0.205% | 27.7175
WF-04 | 5 | WF-04-T02 → WF-04-T01 | 5 | 19 | 20 | 334.6958 | 352.3114 | 500 kcmil | 400.7111 | 87.92% | 0.616 | 0.14697 | 0.14738 | 0.1922% | 30.4253
WF-04 | 6 | WF-04-T01 → SUBSTATION 34.5 kV BUS | 6 | 22.8 | 24 | 401.635 | 422.7737 | 750 kcmil | 454.524 | 93.01% | 5 | 0.099043 | 0.13769 | 1.382% | 239.6507
WF-04 TOTAL |  |  |  | 22.8 |  | 401.635 | 422.7737 | [6 empty] | 2.46% | 352.1381 | 1.544%
Sum of feeder P (MW) |  |  |  | 102.6
Sum of feeder I @1.0 pu (A) | [5 empty] | 1807.3574
WTG count check |  |  | 27 | OK — 27 WTGs
Section k carries k WTGs; k = n is the home-run into the substation. ΔV is the steady-state voltage rise from the bus to the remote WTG at PF_WTG (lagging export).
Home-run sizing within the substation approach corridor is governed by mutual heating — home-run (k = n) is sized against the 4-circuit/2.0 m grouped ampacity on sheet "Cable_Sensitivity" (named range GRP_AMP).
Lengths are ILLUSTRATIVE ONLY (no layout provided). Replace L_INT/L_HR or enter per-section lengths in column L when the layout is issued.

## Cable_Sensitivity
Ampacity sensitivity to soil resistivity and 4-circuit grouping (computed by calc.py — same IEC 60287 model)
PRELIMINARY ENGINEERING — NOT FOR CONSTRUCTION ¦ Rev P0 ¦ 2026-10-13
Case | 1/0 AWG | 4/0 AWG | 350 kcmil | 500 kcmil | 750 kcmil | 1000 kcmil | 1250 kcmil
Single circuit, ρ = 0.9 K·m/W | 193 | 282 | 371 | 449 | 556 | 645 | 719
Single circuit, ρ = 1.0 K·m/W | 186 | 271 | 356 | 431 | 533 | 617 | 688
Single circuit, ρ = 1.2 K·m/W | 174 | 253 | 332 | 401 | 495 | 572 | 637
Single circuit, ρ = 1.5 K·m/W | 160 | 232 | 303 | 365 | 450 | 519 | 578
Single circuit, ρ = 2.0 K·m/W | 142 | 206 | 268 | 322 | 396 | 457 | 507
4 trefoils flat, 1.0 m spacing, ρ = 1.2 (centre circuit) | 149 | 215 | 279 | 335 | 411 | 472 | 524
4 trefoils flat, 2.0 m spacing, ρ = 1.2 (centre circuit) | 162 | 235 | 307 | 369 | 455 | 524 | 582
4 trefoils flat, 3.0 m spacing, ρ = 1.2 (centre circuit) | 168 | 243 | 318 | 383 | 472 | 545 | 607
Values in amperes; 90 °C conductor, 25 °C ambient, 1.0 m depth, 100 % LF. Static values — regenerate with calc.py if inputs change.

## SC_Withstand
Short-circuit withstand — ICEA P-32-382 adiabatic method
PRELIMINARY ENGINEERING — NOT FOR CONSTRUCTION ¦ Rev P0 ¦ 2026-10-13
Conductor (Al): (I/A)²·t = 0.0125·log10[(T2+228)/(T1+228)], A in cmil, T1 = 90 °C, T2 = 250 °C
Screen (Cu), ICEA P-45-482 simplified adiabatic: (I/A)²·t = 0.0297·log10[(T2+234)/(T1+234)], T1 = 80 °C, T2 = 200 °C (jacket-limited, confirm with vendor)
Size | A (kcmil) | I @0.10 s (kA) | I @0.25 s (kA) | I @0.50 s (kA) | I @1.0 s (kA)
1/0 AWG | 105.5639 | 15.7021 | 9.9309 | 7.0222 | 4.9654
4/0 AWG | 211.5619 | 31.4688 | 19.9026 | 14.0733 | 9.9513
350 kcmil | 349.906 | 52.0468 | 32.9173 | 23.276 | 16.4586
500 kcmil | 500.0912 | 74.3861 | 47.0459 | 33.2665 | 23.523
750 kcmil | 749.9395 | 111.5498 | 70.5503 | 49.8866 | 35.2751
1000 kcmil | 999.9851 | 148.7429 | 94.0732 | 66.5198 | 47.0366
1250 kcmil | 1250.0307 | 185.9359 | 117.5962 | 83.1531 | 58.7981
Screen withstand (kA) for As (mm²) = |  | 36.4133
|  | t = 0.10 s | t = 0.25 s | t = 0.50 s | t = 1.0 s
|  | 14.6829 | 9.2863 | 6.5664 | 4.6431
Required Cu screen area (mm²) | I_fault (kA) | t = 0.25 s | t = 0.50 s | t = 1.0 s
| 5 | 19.606 | 27.727 | 39.2119
| 10 | 39.2119 | 55.454 | 78.4238
| 15 | 58.8179 | 83.1811 | 117.6358
| 20 | 78.4238 | 110.9081 | 156.8477
Ground-fault current at the 34.5 kV bus and its division between screen, counterpoise and earth are NOT KNOWN — requires short-circuit study and grounding-transformer selection.

## BESS_Feeders
BESS feeder currents (4 existing feeders) — PCS configuration not provided
PRELIMINARY ENGINEERING — NOT FOR CONSTRUCTION ¦ Rev P0 ¦ 2026-10-13
Quantity | Equation | Value | Unit
BESS S at MV (screening) | S = P/PF | 105.2632 | MVA
Per-feeder P | P/N | 25 | MW
Per-feeder S | S/N | 26.3158 | MVA
Per-feeder current @1.0 pu | S/(√3V) | 440.3892 | A
Per-feeder current @V_MIN |  | 463.5676 | A
Total BESS current @1.0 pu |  | 1761.5569 | A
Duration at rated power | E/P | 2 | h
Actual-PCS method (to be completed when BESS design data are released):
Feeder | No. PCS/MVT blocks (O) | PCS rating each (MVA) (O) | Feeder S (MVA) | Feeder I @1.0 pu (A) | Feeder I @V_MIN (A)
BF-01 |  |  | 0 | 0 | 0
BF-02 |  |  | 0 | 0 | 0
BF-03 |  |  | 0 | 0 | 0
BF-04 |  |  | 0 | 0 | 0

## GSU_Sizing
GSU sizing at 100 MW POI export/import with ±0.95 PF at high side (candidate 125 MVA)
PRELIMINARY ENGINEERING — NOT FOR CONSTRUCTION ¦ Rev P0 ¦ 2026-10-13
Quantity | Equation | Value | Unit
Q required at HV (each direction) | Q = P·tan(acos PF) | 32.8684 | Mvar
S at HV | √(P²+Q²) | 105.2632 | MVA
GSU HV rated current | S_GSU/(√3·115) | 627.5546 | A
GSU MV rated current | S_GSU/(√3·34.5) | 2091.8488 | A
GSU MV current @V_MIN |  | 2201.9461 | A
Max POI current @0.95 pu | S_HV/(√3·0.95·115) | 556.2811 | A
Infinite-bus 3φ fault via GSU at MV | I_MV,r / Z | 20.9185 | kA
Infinite-bus 3φ fault via GSU at HV (grid side excluded) | I_HV,r / Z | 6.2755 | kA
V_HV (pu) | Q sign (+ supply / − absorb) | P_HV (MW) | Q_HV (Mvar) | I (pu of S_GSU) | Equivalent MVA | Loading % | Q loss (Mvar) | P loss (MW) | P_MV (MW) | Q_MV (Mvar) | S_MV (MVA)
0.95 | 1 | 100 | 32.8684 | 0.88643 | 110.8033 | 88.64% | 9.8219 | 0.39288 | 100.3929 | 42.6903 | 109.0926
0.95 | -1 | 100 | -32.8684 | 0.88643 | 110.8033 | 88.64% | 9.8219 | 0.39288 | 100.3929 | -23.0465 | 103.0042
1 | 1 | 100 | 32.8684 | 0.84211 | 105.2632 | 84.21% | 8.8643 | 0.35457 | 100.3546 | 41.7327 | 108.686
1 | -1 | 100 | -32.8684 | 0.84211 | 105.2632 | 84.21% | 8.8643 | 0.35457 | 100.3546 | -24.0041 | 103.1855
1.05 | 1 | 100 | 32.8684 | 0.80201 | 100.2506 | 80.2% | 8.0402 | 0.32161 | 100.3216 | 40.9086 | 108.3418
1.05 | -1 | 100 | -32.8684 | 0.80201 | 100.2506 | 80.2% | 8.0402 | 0.32161 | 100.3216 | -24.8283 | 103.3483
Max equivalent MVA |  |  |  |  | 110.8033
Margin of S_GSU over max equivalent MVA |  |  |  |  | 12.81%
Import (charging) case: identical ¦S¦ at HV ⇒ same current loading; Q-loss sign convention unchanged.
Equivalent MVA = I × √3 × V_rated (thermal duty is current-driven).
Alternative top rating (MVA) | Loading @ 0.95 pu, 0.95 PF
100 | 110.8%
112 | 98.93%
115 | 96.35%
125 | 88.64%
140 | 79.15%

## Fault_Screening
34.5 kV bus three-phase fault screening (parametric — utility fault data not provided)
PRELIMINARY ENGINEERING — NOT FOR CONSTRUCTION ¦ Rev P0 ¦ 2026-10-13
S_sc grid (MVA) | Z_GSU (pu) | Z_sys (pu on S_GSU) | I grid via GSU (kA) | I wind (kA) | I BESS (kA) | I total (kA) | vs 40 kA
2000 | 0.08 | 0.0625 | 14.6796 | 9.0368 | 2.1139 | 25.8303 | ≤ 40 kA
2000 | 0.1 | 0.0625 | 12.8729 | 9.0368 | 2.1139 | 24.0236 | ≤ 40 kA
2000 | 0.12 | 0.0625 | 11.4622 | 9.0368 | 2.1139 | 22.6128 | ≤ 40 kA
4000 | 0.08 | 0.03125 | 18.8031 | 9.0368 | 2.1139 | 29.9538 | ≤ 40 kA
4000 | 0.1 | 0.03125 | 15.9379 | 9.0368 | 2.1139 | 27.0886 | ≤ 40 kA
4000 | 0.12 | 0.03125 | 13.8304 | 9.0368 | 2.1139 | 24.9811 | ≤ 40 kA
8000 | 0.08 | 0.015625 | 21.8755 | 9.0368 | 2.1139 | 33.0262 | ≤ 40 kA
8000 | 0.1 | 0.015625 | 18.0917 | 9.0368 | 2.1139 | 29.2423 | ≤ 40 kA
8000 | 0.12 | 0.015625 | 15.4238 | 9.0368 | 2.1139 | 26.5744 | ≤ 40 kA
1000000000 | 0.08 | 1.25e-07 | 26.1481 | 9.0368 | 2.1139 | 37.2987 | ≤ 40 kA
1000000000 | 0.1 | 1.25e-07 | 20.9185 | 9.0368 | 2.1139 | 32.0691 | ≤ 40 kA
1000000000 | 0.12 | 1.25e-07 | 17.4321 | 9.0368 | 2.1139 | 28.5827 | ≤ 40 kA
S_sc = 1E9 represents an infinite source (upper bound). Generator contributions are bounding arithmetic sums at the bus, ignoring WTG transformer/cable impedance — conservative.
Asymmetry (X/R) and peak/closing duty must be checked per IEEE C37.010 once GSU X/R is known — GSU X/R can exceed the C37.04 standard X/R of 17.

## Ratings
Preliminary equipment rating basis (selected values are PRELIMINARY)
PRELIMINARY ENGINEERING — NOT FOR CONSTRUCTION ¦ Rev P0 ¦ 2026-10-13
Item | Required / calculated | Value | Preliminary selection | Status
34.5 kV main breaker continuous (A) | GSU MV current at 125 MVA, V_MIN | 2201.9461 | 3000 A | Preliminary
34.5 kV wind feeder breaker (A) | Max feeder I @V_MIN | 493.2359 | 1200 A | Preliminary
34.5 kV BESS feeder breaker (A) | Per-feeder I @V_MIN (screening) | 463.5676 | 1200 A | Confirm with BESS design
34.5 kV bus (A) | Max of (Σ wind @V_MIN, Σ BESS @V_MIN, GSU) | 2201.9461 | 3000 A | Preliminary
34.5 kV interrupting (kA sym) | Max of screening cases | 37.2987 | 40 kA (38 kV class, 150 kV BIL) | Confirm by SC study
34.5 kV peak withstand (kA) | 2.6 × I_sc (60 Hz, C37.04) | 104 | 104 kA | Preliminary
115 kV breaker continuous (A) | GSU HV rated current | 627.5546 | 1200 A min. (utility std. may be 2000 A) | U
115 kV breaker interrupting | Utility POI fault level + growth margin | n/a | TBD (40 or 63 kA class) | OPEN — utility data
115 kV arrester MCOV (kV) | ≥ 1.05 × 123/√3 | 74.5648 | ≥ 76 kV MCOV (96 kV duty-cycle) — confirm TOV | Preliminary
34.5 kV arrester MCOV (kV), effectively grounded | ≥ 1.05 × 36.2/√3 | 21.9451 | 22 kV MCOV min. if always effectively grounded; ≥ 36.5 kV MCOV (or TOV-curve justification) if islanded/ungrounded operation possible | Open — grounding study
115 kV BIL | IEEE C57.12.00 / C37.06 class | n/a | 550 kV (450 kV reduced only if insulation coordination permits) | Preliminary
34.5 kV transformer winding BIL | IEEE C57.12.00 | n/a | 200 kV | Preliminary

## POI_Scenarios
POI operating scenarios — net flow vs internal loading (screening losses & aux)
PRELIMINARY ENGINEERING — NOT FOR CONSTRUCTION ¦ Rev P0 ¦ 2026-10-13
Scenario | Wind at WTGs (MW) | BESS at MV (+dis/−chg) (MW) | Wind at POI (MW) | BESS at POI (MW) | Aux (MW) | Net POI (MW, +export) | Within ±100 MW? | Wind feeder ΣI (A) | BESS feeder ΣI (A) | PPC action
S1 Wind full, BESS idle | 102.6 | 0 | 99.522 | 0 | 1 | 98.522 | YES | 1807.3574 | 0 | None — losses keep POI < 100 MW; PPC export limiter armed
S2 Wind full, BESS charging 100 MW | 102.6 | -100 | 99.522 | -101.5 | 1 | -2.978 | YES | 1807.3574 | 1761.5569 | POI ≈ 0 but ALL feeders fully loaded
S3 No wind, BESS discharging 100 MW | 0 | 100 | 0 | 98.5 | 1 | 97.5 | YES | 0 | 1761.5569 | None
S4 Wind 60 MW + BESS 100 MW requested | 60 | 100 | 58.2 | 98.5 | 1 | 155.7 | NO — PPC limit | 1056.9341 | 1761.5569 | PPC must curtail BESS (or wind) to hold ≤ 100 MW
S5 No wind, BESS charging 100 MW requested | 0 | -100 | 0 | -101.5 | 1 | -102.5 | NO — PPC limit | 0 | 1761.5569 | PPC must reduce charge so import (incl. aux & losses) ≤ 100 MW
S6 Wind full + BESS discharge 20 MW requested | 102.6 | 20 | 99.522 | 19.7 | 1 | 118.222 | NO — PPC limit | 1807.3574 | 352.3114 | PPC must hold BESS to ≈ 0–1.5 MW (or curtail wind)
Feeder currents are set by each resource's own output; they are NOT reduced when wind export and BESS charging cancel at the POI (S2).
Max BESS charge with no wind while respecting import limit (MW at PCS): | [5 empty] | 97.5369

## Check
Independent check — workbook formulas vs Python engine (calc.py)
PRELIMINARY ENGINEERING — NOT FOR CONSTRUCTION ¦ Rev P0 ¦ 2026-10-13
Quantity | Workbook | Python | Δ % | Result
WTG S (MVA) | 4 | 4 | 0% | PASS
WTG I 690 V (A) | 3346.9581 | 3346.9581 | 7.729e-09% | PASS
WTG I 34.5 kV (A) | 66.9392 | 66.9392 | -5.301e-07% | PASS
WF-01 home-run I @1.0 pu (A) | 468.5741 | 468.5741 | -1.032e-07% | PASS
WF-04 home-run I @1.0 pu (A) | 401.635 | 401.635 | -3.211e-08% | PASS
Ampacity 1/0 (A) | 174.019 | 174.019 | -1.297e-07% | PASS
Ampacity 500 kcmil (A) | 400.7111 | 400.7111 | -1.049e-07% | PASS
Ampacity 1000 kcmil (A) | 572.0482 | 572.0482 | 7.426e-08% | PASS
Rac 750 kcmil (Ω/km) | 0.099043 | 0.099043 | 0.0001506% | PASS
X 750 kcmil (Ω/km) | 0.13769 | 0.13769 | 0.000159% | PASS
Qc 1000 kcmil (kvar/km) | 110.3651 | 110.3651 | -2.252e-07% | PASS
BESS feeder I (A) | 440.3892 | 440.3892 | 7.944e-08% | PASS
GSU HV rated I (A) | 627.5546 | 627.5546 | 6.749e-08% | PASS
GSU MV rated I (A) | 2091.8488 | 2091.8488 | 1.968e-08% | PASS
GSU max equiv MVA | 110.8033 | 110.8033 | 9e-08% | PASS
Q required at HV (Mvar) | 32.8684 | 32.8684 | -1.467e-06% | PASS
Fault, ∞ bus, Z=0.10 total (kA) | 32.0691 | 32.0691 | -8.123e-05% | PASS
500 kcmil 0.5 s withstand (kA) | 33.2665 | 33.2665 | -7.977e-07% | PASS
WF-01 ΣΔV @ illustrative 5 km (%) | 2.5728 | 2.5728 | -2.227e-06% | PASS
WF-01 losses @ illustrative 5 km (MW) | 0.39042 | 0.39042 | -6.649e-05% | PASS
Grouped ampacity 1000 kcmil (A) | 524.0358 | 524.0358 | -1.971e-09% | PASS
S2 net POI (MW) | -2.978 | -2.978 | -0% | PASS